INFRARED TECHNOLOGY SERVICES

Infrared Inspection Report

| Anomaly Number: | 9 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Severity Rating: | 15 | Inspection Date: | 5/29/2007 | Time: | 1117 |
| Anomaly Location: | Manhole M5, Circuit 3 |  |  |  |  |
| Description: | Middle phase, hot spot at connector plug |  |  |  |  |

| Anomaly Target Temperature: | 86 |  | Rise Above Ambient: | 9 |
| --- | --- | --- | --- | --- |
| Reference Temperature: | 79 |  | Rise Above Reference: | 7 |
| Ambient Temperature: | 77 |  |  |  |

| Recommendation: | Corrective measures should be taken IMMEDIATELY. |
| --- | --- |

| Thermographer: | Lee Wills |  | Emissivity: | .90 |
| --- | --- | --- | --- | --- |
| Camera: | Thermacam PM395 |  | Distance (feet): | 4 |
| Serial Number: | 20401 |  | Wind Speed: | N/A |

| Corrective Action Taken | Date | Signature |
| --- | --- | --- |

Return to Letter

Summary of Anomalies